## 12MW
Parameter | Site 1 | Site 2 | Site 3 | Site 4 | Notes
Representative region | Gulf of Mexico (west portion of Call Area) | Central Atlantic (Call Area E) | New York Bight (Bright Wind Holdings Lease) | California (Humboldt Lease Area)
Representative coordinates | 27.18624, -96.9516 | 37.48358, -73.72925 | 39.53852, -73.1956 | 40.95078, -124.63619 | Just in case we want to pull wind resource data later for a more robust AEP analysis
Substructure technology | Fixed - Monopile | Floating - semisubmersible | Fixed - Monopile | Floating - semisubmersible | Jackets could be the preferred fixed technology choice in Gulf due to softer soils, breaking waves, and proximity to oil & gas labor force with experience building these types of structures. In process of implementing updated jacket cost module. Expected Q4 and could revisit then.
Plant capacity | 996 MW | 996 MW | 996 MW | 996 MW | 83 turbines
Turbine rating | 12 MW | 12 MW | 12 MW | 12 MW
Turbine layout | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | simplistic
Approx. water depth | 45 m | 2000 m | 40 m | 850 m
Approx. distance to port | 80 km | 110 km | 100 km | 55 km
Approx. distance to export cable landfall | 85 km | 110 km | 80 km | 45 km
Onshore spur length | 5 km | 5 km | 5 km | 5 km
Export cable voltage | 220 kV | 220 kV | 220 kV | 220 kV
Array cable voltage | 66kV | 66kV | 66kV | 66kV
ORCA mean wind speed (100m WTK) | 8.8 m/s |  | ~9.15 m/s | ~10 | NY Bight was 9-9.25 m/s
ORCA GCF | 55.6% | 0.51% | 55.4% | 53.1% | I don't believe this is CA20
Assumed NCF | 44.5% | 49% | 44.5% | 49% | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
ORCA Port | Gulf Marine Fabricators | Ocean City | Brooklyn Marine Terminal | Humboldt Bay
Fixed charge rate (nominal) | 7.64% | 7.64% | 7.64% | 7.64% | From 2020 COE Review. There could be a case for slight differences in FCR between fixed and floating, but I can point to a justification to keep them the same. This also helps keep it simple
Fixed charge rate (real) | 5.82% | 5.82% | 5.82% | 5.82% | From 2020 COE Review. The argument the ATB made this year was that while short-term inflation is impacting prices, they don't have any basis to support changing the long-term average inflation rate from 2.5%.
Costs (all reported in 2020 USD with nominal FCR) | Site 1 | Site 2 | Site 3 | Site 4
OpEx, $/kW-yr | 115 | 92 | 115 | 92 | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
Array System | 67 | 169 | 66 | 108
Export System | 90 | 58 | 85 | 25
Substructure | 577 | 1051 | 558 | 1051
Mooring System | 0 | 1288 | 0 | 523.0315 | Monopiles have 0 because no mooring lines.
Offshore Substation | 233 | 234 | 234 | 234
Scour Protection | 17.5 | 0 | 17.74 | 0 | Semisubs have 0 because no scour protection.
Array System Installation | 32 | 42 | 32.0408 | 36
Export System Installation | 178 | 175 | 178 | 175
Offshore Substation Installation | 4 | 5 | 4 | 4
Scour Protection Installation | 38 | 0 | 44 | 0 | Semisubs have 0 because no scour protection.
Substructure Installation | 55 | 76 | 56 | 62
Turbine Installation | 96 | 0 | 98 | 0 | Semisub turbine installation is included in Substructure Installation because of tow-out installation strategy
Mooring System Installation | 0 | 145 | 0 | 93 | Monopiles have 0 because no mooring lines.
BOS | 1387.5 | 3243 | 1372.7808 | 2311.0315
construction_insurance_capex | 31 | 52 | 31 | 42
decomissioning_costs | 69 | 76 | 71 | 63
construction_financing | 133 | 220 | 132 | 175
procurement_contingency_costs | 131 | 235 | 130 | 186
install_contingency_costs | 139 | 153 | 142 | 127
project_completion_capex | 31 | 52 | 31 | 42
Soft | 534 | 788 | 537 | 635
Turbine CapEx | 1300 | 1300 | 1300 | 1300 | From OSW Market Report 2021 Edition. I wouldn't be surprised if these have increased since then. There could be a case for increasing floating turbine CapEx ~5% for hardening, but again keeping it simple for now
Total CapEx | 3221 | 5332 | 3209 | 4244
LCOE | 93 | 116 | 92 | 97 | Nominal
check Total CapEx | 3221.5 | 5331 | 3209.7808 | 4246.0315

## 15MW
Parameter | Site 1 | Site 2 | Site 3 | Site 4 | Notes
Representative region | Gulf of Mexico (west portion of Call Area) | Central Atlantic (Call Area E) | New York Bight (Bright Wind Holdings Lease) | California (Humboldt Lease Area)
Representative coordinates | 27.18624, -96.9516 | 37.48358, -73.72925 | 39.53852, -73.1956 | 40.95078, -124.63619 | Just in case we want to pull wind resource data later for a more robust AEP analysis
Substructure technology | Fixed - Monopile | Floating - semisubmersible | Fixed - Monopile | Floating - semisubmersible | Jackets could be the preferred fixed technology choice in Gulf due to softer soils, breaking waves, and proximity to oil & gas labor force with experience building these types of structures. In process of implementing updated jacket cost module. Expected Q4 and could revisit then.
Plant capacity | 996 MW | 996 MW | 996 MW | 996 MW | 83 turbines
Turbine rating | 15 MW | 15 MW | 15 MW | 15 MW
Turbine layout | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | simplistic
Approx. water depth | 45 m | 2000 m | 40 m | 850 m
Approx. distance to port | 80 km | 110 km | 100 km | 55 km
Approx. distance to export cable landfall | 85 km | 110 km | 80 km | 45 km
Onshore spur length | 5 km | 5 km | 5 km | 5 km
Export cable voltage | 220 kV | 220 kV | 220 kV | 220 kV
Array cable voltage | 66kV | 66kV | 66kV | 66kV
ORCA mean wind speed (100m WTK) | 8.8 m/s |  | ~9.15 m/s | ~10 | NY Bight was 9-9.25 m/s
ORCA GCF | 55.6% | 0.51% | 55.4% | 53.1% | I don't believe this is CA20
Assumed NCF | 46.1% | 50% | 46.1% | 50% | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
ORCA Port | Gulf Marine Fabricators | Ocean City | Brooklyn Marine Terminal | Humboldt Bay
Fixed charge rate (nominal) | 7.64% | 7.64% | 7.64% | 7.64% | From 2020 COE Review. There could be a case for slight differences in FCR between fixed and floating, but I can point to a justification to keep them the same. This also helps keep it simple
Fixed charge rate (real) | 5.82% | 5.82% | 5.82% | 5.82% | From 2020 COE Review. The argument the ATB made this year was that while short-term inflation is impacting prices, they don't have any basis to support changing the long-term average inflation rate from 2.5%.
Costs (all reported in 2020 USD with nominal FCR) | Site 1 | Site 2 | Site 3 | Site 4
OpEx, $/kW-yr | 103 | 83 | 103 | 83 | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
Array System | 62 | 144 | 62 | 95.6
Export System | 91 | 59 | 86 | 26
Substructure | 561 | 980 | 543 | 980
Mooring System | 0 | 1030 | 0 | 418 | Monopiles have 0 because no mooring lines.
Offshore Substation | 235 | 235 | 235 | 235
Scour Protection | 17 | 0 | 17 | 0 | Semisubs have 0 because no scour protection.
Array System Installation | 26 | 35 | 26 | 30
Export System Installation | 178 | 175 | 178 | 175
Offshore Substation Installation | 4 | 5 | 4 | 4
Scour Protection Installation | 30 | 0 | 35 | 0 | Semisubs have 0 because no scour protection.
Substructure Installation | 47 | 61 | 48 | 50
Turbine Installation | 85 | 0 | 89 | 0 | Semisub turbine installation is included in Substructure Installation because of tow-out installation strategy
Mooring System Installation | 0 | 116 | 0 | 73 | Monopiles have 0 because no mooring lines.
BOS | 1336 | 2840 | 1323 | 2086.6
construction_insurance_capex | 30 | 47 | 30 | 39
decomissioning_costs | 64 | 67 | 65 | 57
construction_financing | 129 | 199 | 129 | 163
procurement_contingency_costs | 130 | 214 | 128 | 175
install_contingency_costs | 127 | 134 | 131 | 114
project_completion_capex | 30 | 47 | 30 | 39
Soft | 510 | 708 | 513 | 587
Turbine CapEx | 1300 | 1300 | 1300 | 1300 | From OSW Market Report 2021 Edition. I wouldn't be surprised if these have increased since then. There could be a case for increasing floating turbine CapEx ~5% for hardening, but again keeping it simple for now
Total CapEx | 3146 | 4848 | 3137 | 3971
LCOE | 85 | 103 | 85 | 88 | Nominal
check Total CapEx | 3146 | 4848 | 3136 | 3973.6

## 18MW
Parameter | Site 1 | Site 2 | Site 3 | Site 4 | Notes
Representative region | Gulf of Mexico (west portion of Call Area) | Central Atlantic (Call Area E) | New York Bight (Bright Wind Holdings Lease) | California (Humboldt Lease Area)
Representative coordinates | 27.18624, -96.9516 | 37.48358, -73.72925 | 39.53852, -73.1956 | 40.95078, -124.63619 | Just in case we want to pull wind resource data later for a more robust AEP analysis
Substructure technology | Fixed - Monopile | Floating - semisubmersible | Fixed - Monopile | Floating - semisubmersible | Jackets could be the preferred fixed technology choice in Gulf due to softer soils, breaking waves, and proximity to oil & gas labor force with experience building these types of structures. In process of implementing updated jacket cost module. Expected Q4 and could revisit then.
Plant capacity | 996 MW | 996 MW | 996 MW | 996 MW | 83 turbines
Turbine rating | 18 mW | 18 MW | 18 MW | 18 MW
Turbine layout | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | 7D x 7D square grid | simplistic
Approx. water depth | 45 m | 2000 m | 40 m | 850 m
Approx. distance to port | 80 km | 110 km | 100 km | 55 km
Approx. distance to export cable landfall | 85 km | 110 km | 80 km | 45 km
Onshore spur length | 5 km | 5 km | 5 km | 5 km
Export cable voltage | 220 kV | 220 kV | 220 kV | 220 kV
Array cable voltage | 66kV | 66kV | 66kV | 66kV
ORCA mean wind speed (100m WTK) | 8.8 m/s |  | ~9.15 m/s | ~10 | NY Bight was 9-9.25 m/s
ORCA GCF | 55.6% | 0.51% | 55.4% | 53.1% | I don't believe this is CA20
Assumed NCF | 46.8% | 51% | 46.8% | 51% | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
ORCA Port | Gulf Marine Fabricators | Ocean City | Brooklyn Marine Terminal | Humboldt Bay
Fixed charge rate (nominal) | 7.64% | 7.64% | 7.64% | 7.64% | From 2020 COE Review. There could be a case for slight differences in FCR between fixed and floating, but I can point to a justification to keep them the same. This also helps keep it simple
Fixed charge rate (real) | 5.82% | 5.82% | 5.82% | 5.82% | From 2020 COE Review. The argument the ATB made this year was that while short-term inflation is impacting prices, they don't have any basis to support changing the long-term average inflation rate from 2.5%.
Costs (all reported in 2020 USD with nominal FCR) | Site 1 | Site 2 | Site 3 | Site 4
OpEx, $/kW-yr | 97 | 78 | 97 | 78 | ATB 2022, OpEx based on R&D assumptions with a base year of 2022.
Array System | 59 | 128 | 59 | 87
Export System | 91 | 59 | 86 | 26
Substructure | 548 | 942 | 531 | 942
Mooring System | 0 | 859 | 0 | 349 | Monopiles have 0 because no mooring lines.
Offshore Substation | 235 | 235 | 235 | 235
Scour Protection | 16 | 0 | 16 | 0 | Semisubs have 0 because no scour protection.
Array System Installation | 23 | 30 | 23 | 25
Export System Installation | 178 | 175 | 178 | 175
Offshore Substation Installation | 4 | 5 | 4 | 4
Scour Protection Installation | 25 | 0 | 29 | 0 | Semisubs have 0 because no scour protection.
Substructure Installation | 39 | 51 | 41 | 42
Turbine Installation | 72 | 0 | 75 | 0 | Semisub turbine installation is included in Substructure Installation because of tow-out installation strategy
Mooring System Installation | 0 | 97 | 0 | 62 | Monopiles have 0 because no mooring lines.
BOS | 1290 | 2581 | 1277 | 1947
construction_insurance_capex | 30 | 44 | 30 | 37
decomissioning_costs | 59 | 61 | 60 | 53
construction_financing | 126 | 186 | 126 | 156
procurement_contingency_costs | 129 | 201 | 127 | 168
install_contingency_costs | 117 | 123 | 120 | 105
project_completion_capex | 30 | 44 | 30 | 37
Soft | 491 | 659 | 493 | 556
Turbine CapEx | 1300 | 1300 | 1300 | 1300 | From OSW Market Report 2021 Edition. I wouldn't be surprised if these have increased since then. There could be a case for increasing floating turbine CapEx ~5% for hardening, but again keeping it simple for now
Total CapEx | 3079 | 4540 | 3069 | 3802
LCOE | 81 | 95 | 81 | 83 | Nominal
check Total CapEx | 3081 | 4540 | 3070 | 3803